## Slide 1
DATA SCIENCE IN A
DATA DRIVEN ENERGY ORGANISATION
Thilaksha Silva, PhD
Senior Data Scientist
Citipower, Powercor & United Energy
Shashank Kundapur
Software Developer
Operational Technology Solutions Pty Ltd

## Slide 2
What is Data Science?

## Slide 3: Data Science
3
Big data
Manage and mine the data
Create insights from data
Actionable business outcomes

## Slide 4
Who are we?

## Slide 5: Distribution
5

## Slide 6
Our databases

## Slide 7: Analytics Platform - Meter data
7

## Slide 8: Our Smart Meter Population
8
Over 1.8 million active smart meters in our Advanced Metering Infrastructure (AMI) Smart Meter Network
350 million records per day
65 GB of new data per day and 23.8 TB per year
99.93% of consumption reads delivered daily
We get 5-minute and 10-second voltage, current and power factor profile data of every smart meter in the network providing a time synced real-time snapshot of the whole network
Few ‘000 customers on 1-min profile data collected every 5 min
15 carefully selected alarms to identify potential fault conditions

## Slide 9
We exploit data science, big data and analytics

## Slide 10
LV-DERMS Demand Response Management

## Slide 11
LV-DERMS demand management
The LV-DERMS project was initiated to ease constraints during times of high demand e.g., seasonal peaks:
managing the residential demand during peak periods
  HOW?
    adjust customers’ air conditioners for a few hours
    on a few really hot days over summer when the electricity demand is at its peak
By controlling the customers AC consumption, we control the load on the LV network during peak demand periods to help balance the grid.
  Ensure a safe and reliable network which ultimately prevents customer outages.

## Slide 12
12
Objective
For identified distribution substations, we forecast hourly demand for the next 48 hours
Data
Historic demand
half-hourly aggregated demand from 2018-01-01 to 2020-10-12 for each distribution substation
Historic weather
half-hourly weather observations from 2018-01-01 to 2020-10-12 for all weather zones in Victoria
Forecast weather
hourly weather forecast for the next 14 days for all weather locations in Victoria

## Slide 13



Demand drivers
A random forest regression model is trained given weather and calendar features:
Weather effects
current temperature
current temperature squared
temperature from the same time period of the previous day
temperature from 6hrs before
maximum temperature in the last 24hrs
minimum temperature in the last 24hrs
wind speed
Calendar effects
day of week effect (to handle daily seasonal pattern)
hour of day effect
month of year effect
public holiday effect
school holiday effect
covid effect
Electricity demand can be modelled as a non-linear function of temperature as more electricity is used on cold days due to heating and hot days due to air conditioning.

## Slide 15
Evaluating the quality of model’s predictions
The quality of forecast demand is evaluated using regression metric functions and cross validation score:

## Slide 16
Network Outage Forecasting

## Slide 17: Resource Forecasting & Storm Impact – 2 day ahead forecast
Machine Learning
Forecast
Outages
Faults per area
Trucks required per area
When are Trucks required?
Calls to Call Centre
USAIDI Impact = $
Network load
History + Forecast
Weather Data
12 years of data
DMS Faults Data
Resources requirements
& Input Notification
Central
South
North

## Slide 18
18
Objective
Forecast the number of network outages for regions in the electricity distribution network.
Features
Historical outage data
Historical weather observation
    Temperature
    Wind
    rainfall
Hourly weather forecast
Calendar effects:
    Weekday
    Weekend
    public holiday

## Slide 19
Network Fault Detection

## Slide 20
Neutral Fault Detection

## Slide 21
Neutral Fault
When a Neutral wire of electricity system becomes disconnected or damaged and cannot carry current anymore.
Power flows into the premise via an active cable and leaves via a neutral cable. However, if there is no neutral, this could cause an influx of voltage. A neutral issue can cause serious issues to the equipment which can be irreparable and possible life-threatening situation.
  Causes of Loss of Neutral are weather, animal, poor installation or corrosion
Notes: Information Retrieved from
https://www.thelocalelectrician.com.au/what-is-a-broken-neutral-wire/
https://www.sollatek.com/loss-of-neutral/

## Slide 22: Detect network faults right up to the transformer
22

## Slide 23: Example: Near Real-Time Analytics
  Detection Mechanism
  Based on the smart meter channel reading with voltage and current profile.
  For every drop in voltage, we can clearly see a rise in the current.
  Calculate the number of times this happens in the day and if the thresholds do reach then raise it an as job to fix.
  Outcome of this Jobs
Correlation Between Voltage & Current

## Slide 24: Example: Near Real-Time Analytics
  Detection Mechanism
  Based on the smart meter channel reading with voltage and current profile.
  For every drop in voltage, we can clearly see a rise in the current.
  Calculate the number of times this happens in the day and if the thresholds do reach then raise it an as job to fix.
  Outcome of this Jobs

## Slide 25: Example: Near Real-Time Analytics
  Detection Mechanism
  Effects of DER Devices in Loss of Neutral Detection.
  Voltage and Current exhibit the same behavior.
  For every drop in voltage, we can clearly see a rise in the current.
  We do have to sometime wait for the clouds to clear for the jobs to reach the threshold as the current would be negative.

## Slide 26: Example: Near Real-Time Analytics (High Voltage)
  Detection Mechanism
  Based on the smart meter channel reading with voltage and current profile.
  For every rise in voltage, we record for every over voltage and count the number of time the voltage was over the threshold. If the voltage is too high, we would disconnect the customer
  Outcome of this Jobs/Comments – “Repaired neutral connection at service pole due to corrosion. Tested and re energised meter. Customer is happy appliances now working properly.”

## Slide 27
HV Fuse Issue/Brownout

## Slide 28
Potential Brownout Detection
When the Fuse is Blow or if the HV Conductor is broken we normally have multiple customer on the substation which would see power outage.
Raising Faults to DMS will enable them to track down the exact location of fault.
Helps to act on the fault before the customer calls.

## Slide 29: Example: Near Real-Time Analytics
  Detection Mechanism
  Based on the smart meter channel reading with voltage and current profile.
  For every drop in voltage, we will calculate the number of times the customer saw the voltage drop.
  If certain percentage of customer on the substation notice the issue. We would raise a Potential Brownout Fault.
  Outcome of this Jobs/Comments – “Replaced 15E BA fuse white phase. Caused by possum on TX bushing. Wood pole with animal proofing fitted. NO FIRE.

## Slide 30
System Automation

## Slide 31: Automated Monitoring Of Service Mains

## Slide 32: Automated Monitoring Of Service Mains
  3 deaths across Australia could be attributed to a Loss of Neutral supply
  Regulators across states have increased the required frequency of meter inspections to address this risk
  Regulators across states have increased the required frequency of meter inspections to address this risk
  United Energy needs to inspect 650k services every 10 years:
        Current on-site inspections are costly
        “Frequent” inspections still do not address the risk for failure between inspections. An inspection just detect failures since the last inspection
  In addition, significant cost incurred to investigate customers who report loss of neutral every year, especially if they receive a shock
  Our remote monitoring tool checks and measures the service line quality and associated risks every hour (configurable) to flag changes in service main health.
        658k meters monitored every hour
        Change of health monitored and cases automatically issued to DMS
        No more on-site neutral inspections
        1950 lines proactively fixed since Jan ’16
        Now at 98% success rate
Benefits
  Reduced our annual on-site inspection cost by $’m per year
  Reduced our shock incidents by more than 70%, compared to the last 5 years average

## Slide 33: Network Fault Dispatch – Analytics Raising Jobs to DMS
On Dispatch Supporting details
On Dispatch SMS Customer
DMS Jobs
Customer Service
Raise Job
Job issue
Data/Graphs requests
RTS
DMS
P1
:
P6
SCADA
Analytics
20 Min to 2h
Periodic 5 min AMI Data
AMI
Comms
Field Mobility
iPad
iPad
AMI Meters
ZSS

## Slide 34: Network Fault Dispatch – Analytics making the supply safe
On Dispatch Supporting details
Raise Job
Job issue
Data/Graphs requests
RTS
DMS
P1
:
P6
SCADA
Periodic 5 min AMI Data
Disconnect Supply
Bad
NAP
DMS Jobs
Notify Call Centre
Call Customer
3 – 20+ min
Customer Service
ZSS
AMI
Comms
Field Mobility
iPad
iPad
On Dispatch SMS Customer
AMI Meters

## Slide 35
Value of Real Time 10 Second Data Analytics

## Slide 36
Background Information
Need for Speed
Experienced few cases where customers received shocks or experienced equipment damage after a job has been issued and/or just before a safety disconnect occurred.
Normally noticed after the fault was for around 20 minutes after which the customer was disconnected.
Subsequent Action Taken
  New SIQ firmware deployed to all smart meters upgrading them to have up to 3 x SIQ profiles
  2 Profiles deployed on all smart meters. 5 min, now being read every 15 minutes and 10 second profiles being read on demand as required
  16 “smart” alarms deployed to every smart meter for real time alerts of potential network faults or safety related conditions

## Slide 37: 10 Sec Data Retrieved For As Long As Safety Condition Exists
  Sample Scenario
  5 Min data received up to 19:55 and all normal. Next data due after 20:10
  19:59:01 – Smart Alarm raised from SIQ in communications card
  20:00 – Analytics Team analyses alarm and severity and request 10s profile data from meter
Receive Safety Issue Alarm and request 10s data

## Slide 38: 10 Sec Data Retrieved For As Long As Safety Condition Exists
  Sample Scenario
  5 Min data received up to 19:55 and all normal. Next data due after 20:10
  19:59:01 – Smart Alarm raised from SIQ in communications card
  20:00 – Analytics Team analyses alarm and severity and request 10s profile data from meter
  20:02 – Analytics Team analyses 10s profile data confirm fault and severity and issue a safety disconnect
  20:03:40 – Meter confirmed disconnection was successful, current dropped to 0 Amps and property is now safe
  20:05:14 – Job confirmed being raised in DMS as LV backbone neutral issue (2 properties affected and disconnected)
  20:05 – Analytics Team email notification to all stakeholders and Contact Center
  20:25 – 2nd Notification circulated that customer called back after voice mail and is aware of circumstances
Issue Safety Disconnect
Receive Safety Issue Alarm and request 10s data

## Slide 39: 10 Sec Data Retrieved For As Long As Safety Condition Exists
  20:24 – Notification circulated from Contact Center – tried to contact customer and left voice mail.
  20:25 – 2nd Notification circulated that customer called back and is aware of circumstances
  20:35 – Fault Crew arrive on site
  21:07 – Repaired burnt out neutral @ pole
  21:07 – Condition normal and NAP stop requesting 10 sec data
  21:15 – Power restored
Confirmed meter disconnect
Receive Safety Issue Alarm and request 10s data
Reverts back to
5 min data

## Slide 40: Equivalent 5 Minute Dataset
  The 5 min dataset contains a lot less information (30x less than 10 sec).
  Analyzing only 5 min data arriving every 15 minutes would have taken a lot longer to achieve the same validation and confirmation that it is a true fault and not a false positive

## Slide 41
We make the
network safer,
more reliable and
cheaper.
We produce value
for our customers
through analytics.

## Slide 42
Thank you!
Thilaksha Silva
LinkedIn profile: https://www.linkedin.com/in/thilakshasilva/
Shashank Kundapur
LinkedIn profile: https://www.linkedin.com/in/shashankkundapur/